## Instructions
Department of Education & Early Development (DEED) ASHRAE Standard 90.1-2016 Compliance Checklist
Worksheet Name | Worksheet Description and Instructions
Introduction | This checklist is designed for use by designers, reviewers, and project inspectors. Designers can use it to check themselves to insure the items listed are included in design. Reviewers can use it to check for design and provide feedback on design. Inspectors will have design parameters to inspect and assure the owner that the project is delivering the construction project requirementss. Note: These are the more common items that may be included in school construction or renovation projects. Other provisions within Standard 90.1-2016 may also apply.
Basic Instructions for Use | Initially the owner and consultant will review the checklist and indicate to the department what items in the checklist do not pertain to the project. Upon agreement those items will be struckthrough in the Description column and "Does not Pertain" will be entered in the Comment column. If, as design progresses, any item is determined to be required, the strikethrough will be removed and the comment changed to reflect the rationale.
Cover sheet | Include department project name, number, school district, and facility(ies). Also, include the climate zone (note: there are new zones compared to 90.1-2010).
Design Plan Review | This tab will be used throughout the design phase to document design and contract document elements needed for compliance. The first column indicates the design system.The second column lists the ASHRAE Standard 90.1 sections associated with the item in review. The third column is a description of the item. The fourth column is to document the appropriate design value for the item, as applicable. The fifth column is to indicate if the documents are in compliance, and the sixth column is for any comments including the location in the plans/specs. This sheet is to confirm that the consultant has supplied all required calculations for review. This will allow the department and owner to determine if Standard 90.1 is being met and whether designs may be under designed and not delivering requirements to meet needs or if there is overdesign that may increase construction and operating costs.
Foundation Inspection | The first column lists the ASHRAE Standard 90.1 requirements associated with the item in review. The second column is a description of the item. The third column is to enter the designed value of insulation, etc.; the fourth column is for field inspection verifying that construction meets requirements. The fifth column is to indicate whether the design and installation meets requirements, and the sixth column is for any comments. This sheet is to review design and installation. The cells with "NA" do not require insertion of values.
Framing Inspection | The first column lists the ASHRAE Standard 90.1 requirements associated with the item in review. The second column is a description of the item. The third column is to enter the designed value of insulation, etc.; the fourth column is for field inspection verifying that construction meets requirements. The fifth column is the indicate whether the design and installation meets requirements and the sixth column is for any comments. This sheet is to review design and installation. The cells with "NA" do not require insertion of values.
Insulation Inspection | The first column lists the ASHRAE 90.1 codes associated with the item in review. The second column is a description of the item. The third column is to enter the designed value of insulation, etc.; the fourth column is for field inspection verifying that construction meets requirements. The fifth column is the indicate whether the design and installation meets requirements and the sixth column is for any comments. This sheet is to review design and installation. The cells with "NA" do not require insertion of values.
Plumbing Inspection | The first column lists the ASHRAE Standard 90.1 codes associated with the item in review. The second column is a description of the item. The third column is to indicate if the documents are in compliance and the fourth column is for any comments. This sheet is to confirm that all requirements are inspected and confirmed for plumbing.
Mechanical Inspection | The first column lists the ASHRAE Standard 90.1 codes associated with the item in review. The second column is a description of the item. The third column is to indicate if the documents are in compliance and the fourth column is for any comments. This sheet is to confirm that all mechanical designs meet Standard 90.1 and are included in the documents and that installation meets those designs.
Electrical Inspection | The first column lists the ASHRAE Standard 90.1 codes associated with the item in review. The second column is a description of the item. The third column is to indicate if the documents are in compliance and the fourth column is for any comments. This sheet is to confirm that all electrical designs meet Standard 90.1 and are included in the documents and that installation meets those designs.
Final Inspection | The first column lists the ASHRAE Standard 90.1 codes associated with the item in review. The second column is a description of the item. The third column is to indicate if the documents or installation are in compliance and the fourth column is for any comments. This sheet is to confirm that all closeout documents are provided and all final inspections and commissioning is completed.
end instructions

## Cover
Department of Education & Early Development (DEED) ASHRAE Standard 90.1-2016 Compliance Checklist
Project Number:
Project Name:
School District:
Facility(ies):
Climate Zone:

## Design Plan Review
System | 90.1-2016 Section # | Description | Design Value | Complies? (Yes/No) | Comments
Envelope | 4.2.2, 5.4.3.1.1, 5.7 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the building envelope and document where exceptions are claimed. Envelope tradeoff option (5.6) or energy cost budget (11) submitted for buildings with vertical fenestration area >40% or skylight area >5%. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.5.3.3 | Below-grade wall insulation R-value. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.5.3.5 | Slab edge insulation R-value. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.8.1.7 | Exterior insulation protected against damage, sunlight, moisture, wind, landscaping, and equipment maintenance activities. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.8.1.7.3 | Insulation in contact with the ground has <=0.3% water absorption rate per ASTM C272. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 6.3.2, 6.4.4.1, 6.4.4.2 | Piping, ducts and plenum are insulated and sealed when installed in or under a slab. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 6.4.3.7 | Freeze protection and snow/ice melting system are automatically controlled to shut-off at the required temperatures.. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 6.4.4.1.5 | Bottom surface of floor structures incorporating radiant heating insulated to a minimum of R-3.5. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.4.3.4 | Vestibules are installed where building entrances separate conditioned space from the exterior, and meet exterior envelope requirements. Doors have self-closing devices, and are >=7 ft apart. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.5.4.3 | Vertical fenestration U-Factor. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.5.4.3 | Skylight fenestration U-Factor. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.5.4.4.1 | Vertical fenestration SHGC value. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.5.4.4.2 | Skylight SHGC value. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.5.3.6 | U-factor of opaque doors associated with the building thermal envelope meets requirements. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.4.3 | All requirements for continuous air-barrier are met including identifying in the drawings for sealing. Project includes required pressure testing | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.5.3.1 | Roof R-value. For some roof systems, verification may need to occur during Framing Inspection. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.8.1.3 | Blown or poured loose-fill insulation is installed only where the roof slope is <=3 in 12. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.5.3.1 | Skylight curbs insulated to the level of roofs with insulation above deck or R-5. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.5.3.2 | Above-grade wall insulation R-value. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.5.3.4 | Floor insulation R-value. |  |  | Enter the Design Value and provide supporting calculations.
Envelope | 5.8.1.4 | Eaves are baffled to deflect air above the insulation. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.8.1.5 | Insulation is installed in substantial contact with the inside surface separating conditioned space from unconditioned space. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.8.1.7 | Exterior insulation is protected from damage with a protective material. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.8.1.7.1 | Attics and mechanical rooms have insulation protected where adjacent to attic or equipment access. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.8.1.8 | Insulation intended to meet the roof insulation requirements cannot be installed on top of a suspended ceiling. Mark this requirement compliant if insulation is installed accordingly. | NA |  | Enter a reference as to where this is covered in the project documents.
Envelope | 5.4.3.3 | Weatherseals installed on all loading dock cargo doors. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 4.2.2, 6.4.4.2.1, 6.7.2 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the mechanical systems and equipment and document where exceptions are claimed. Submit heat and ventilation calculations. |  |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.4.3 | Service hot-water piping systems insulated per table 6.8.3-1. Note: where piping is installed in or under a slab, verification may need to occur during Foundation Inspection. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.4.4.1 | Temperature controls installed on service water heating systems (<=120 ºF to maximum temperature for intended use). | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.4.4.2 | Controls shall be installed to automatically shut off the recirculating hot water and heat trace systems. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.4.6 | Heat traps installed on non-circulating storage water tanks. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.4.1 | Stair and elevator shaft vents have motorized dampers that automatically close. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.4.2, 6.4.3.4.3 | Outdoor air and exhaust systems have motorized dampers that automatically shut when not in use and meet maximum leakage rates. Check gravity dampers where allowed. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.4.4 | Ventilation fans >0.75 hp have automatic controls to shut off fan when not required. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.8 | Demand control ventilation provided for spaces >500 ft2 and >25 people/1000 ft2 occupant density and served by systems with air side economizer, auto modulating outside air damper control or design airflow >3,000 cfm. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.9 | Heating for vestibules are controlled to shut off heating system when outdoor temperature is above 45F. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.4.1.1 | Insulation exposed to weather protected from damage. Insulation outside of the conditioned space and associated with cooling systems is vapor retardant. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.4.1.2 | HVAC ducts and plenums insulated (R-Value). Reference Tables 6.8.2. | NA |  | Enter the Design Value and provide supporting calculations.
Mechanical | 6.4.4.1.3 | HVAC piping insulation thickness. Reference tables 6.8.3-1&2 | NA |  | Enter the Design Value and provide supporting calculations.
Mechanical | 6.4.4.1.4 | Thermally ineffective panel surfaces of sensible heating panels have insulation >= R-3.5. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.5 | Site-assembled or site-constructed walk-in coolers and walk-in freezers shall conform to 6.4.5 | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.1, 6.5.1.1.1, 6.5.1.1.2, 6.5.1.1.3, 6.5.1.3 | Air economizers provided where required, meet the requirements for design capacity, control signal, and high-limit shut-off and integrated economizer control. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.1.1.5 | Means provided to relieve excess outside air during economizer operation. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.1.2, 6.5.1.2.1, 6.5.1.2.2, 6.5.1.3 | Water economizers provided where required, meet the requirements for design capacity, maximum pressure drop and integrated economizer control and heating system impact. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.1.4 | Economizer operation will not increase heating energy use during normal operation. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.2.1 | Zone controls can limit simultaneous heating and cooling and sequence heating and cooling to each zone. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.2.2.3 | Hydronic heat pump systems connected to a common water loop meet heat rejection and heat addition requirements. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.2.3 | Dehumidification controls provided to prevent reheating, recooling, mixing of hot and cold airstreams or concurrent heating and cooling of the same airstream. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.3.1.2 | HVAC fan motors not larger than the first available motor size greater than the bhp. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.3.2.3 | Reset static pressure setpoint for DDC controlled VAV boxes reporting to central controller based on the zones requiring the most pressure. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.3.3 | Multiple zone VAV systems with DDC of individual zone boxes shall include means to automatically reduce outdoor air in response to changes in ventilation efficiency. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.4.2 | HVAC pumping systems with three or more control valves Shall be designed for variable fluid flow. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.4.3.2 | When aboiler plant includes more than one boiler, provisions shall be made so that all flow through the boiler is automatically shut off when the boiler is shut down. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.4.4 | Temperature reset by representative building loads in pumping systems for chiller and boiler systems >300,000 Btu/h. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.4.5.2 | Hydronic heat pumps and water-cooled unitary air conditioners with pump systems >5 hp have controls or devices to reduce pump motor demand of no more than 30% of design wattage at 50% of design water flow. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.5.2.1 | The fan system on a heat rejection device powered by an individual motor or an array of motors with a connected load, including motor service factor, totaling 5 hp or more shall have controls and/or devices that shall result in fan motor demand of no more than 30% of design wattage at 50% of design air flow. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.6.1 | Exhaust air energy recovery on systems required by Table 6.5.6.1-1 or 6.5.6.1-2. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.7.2.1 | Replacement air introduced directly into the hood cavity of kitchen exhaust hoods shall not exceed 10% of the hood exhaust airflow rate. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.7.2.2 | If a kitchen/dining facility has a total kitchen hood exhaust airflow rate >5,000 cfm, meet exhaust rate requirements of table 6.5.7.2.2. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.7.1.4 | If a kitchen/dining facility has a total kitchen hood exhaust airflow rate >5,000 cfm, then it shall meet one of the options 6.5.7.2.3 a,b or c. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.7.3 | Fume hoods exhaust systems >=5,000 cfm shall include at least one of the features of 6.5.7.3 a, b or c. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.5.8.1 | Unenclosed spaces that are heated use only radiant heat. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.4.2 | Service water heating equipment meets efficiency requirements of table 7.8. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.4.4.3 | Temperature controlling means shall be provided to limit the maximum temperature of water delivered from lavetory faucets to 110 F | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.4.4.4 | When used to maintain storage tank water temperature, recirculating pumps shall be equiped with controls tlimiting operation to a period from the start of the heating cycle to a maximum of five minutes after the end of the heating cycle. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.5.1 | The use of a gas-fired or oil-fired space heating boiler system otherwise complying with section 6 to provide the total space heating and service water heating for a building is allowed if one of the conditions 7.5.1 a, b or c are met. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 7.5.2 | Service water heating equipment used for space heating complies with the service water heating equipment requirements. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.1.1 | Heating and cooling to each zone is controlled by a thermostatic controls. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.3.1 | HVAC systems shall be equipped with at least one automatic shutdown control under 6.4.3.3.1 a, b, c or d. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.3.2 | Heating systems shall be equipped with controls capable of and configured to automatically restart and temporarily operate the system as required to maintain zone temperatures above an adjustable heating set point at least 10°F below the occupied heating set point. Cooling systems shall be equipped with controls capable of and configured to automatically restart and temporarily operate the mechanical cooling system as required to maintain zone temperatures below an adjustable cooling set point at least 5°F above the occupied cooling set point or to prevent high space humidity levels. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.3.3 | Individual heating and cooling systems with setback controls and DDC shall have optimum start controls. The control algorithm shall, as a minimum, be a function of the difference between space temperature and occupied set point, the outdoor temperature, and the amount of time prior to scheduled occupancy. Mass radiant floor slab systems shall incorporate floor temperature into the optimum start algorithm. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 6.4.3.5 | Heat pump controls prevent supplemental electric resistance heat from coming on when not needed. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 4.2.2, 6.7.2.3, 6.7.2.4 | Plans document that systems are to be balanced in accordance with generally accepted engineering standards for conditioned areas greater than 5,000 square feet. Detailed instructions for HVAC systems commissioning included on the plans or specifications for >=50,000 ft2. | NA |  | Enter a reference as to where this is covered in the project documents.
Mechanical | 4.2.2, 7.7.1, 10.4.2 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the service water heating systems and equipment and document where exceptions are claimed. Service water pressure booster systems designed with pressure sensors, pressure reducers, and flow controls. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 4.2.2 8.7 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the electrical systems and equipment and document where exceptions are claimed. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 8.4.1 | The feeder conductors and branch circuits combined shall be sized for a maximum of 5% voltage drop. If contractor alters from design, contractor to provide voltage drop calculations. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 8.4.2 | At least 50% of all 125 volt 15- and 20-Amp receptacles, as required by 8.4.2, and 25% of the circuits for modular furniture are controlled by an automatic control device. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 8.4.3 | Power monitoring and reporting devices shall be provided to address loads in paragraphs a. through e. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 4.2.2, 9.7 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the interior lighting systems and equipment and document where exceptions are claimed. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 9.4.1.1 | Automatic lighting control to shut off all building lighting installed in buildings in compliance with 9.4.1.1. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 4.2.2, 9.7 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the exterior lighting systems and equipment and document where exceptions are claimed. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 9.4.1.4 | Automatic lighting controls for exterior lighting installed. | NA |  | Enter a reference as to where this is covered in the project documents.
Electrical | 9.4.3 | Lighting control devices and control systems shall be tested to ensure that control hardware and software are calibrated, adjusted, programmed, and in proper working condition in accordance with the construction documents and manufacturer’s installation instructions. When occupant sensors, time switches, programmable schedule controls, or photosensors are installed, at a minimum, the procedures in subsections a. - c. shall be performed. | NA |  | Enter a reference as to where this is covered in the project documents.

## Foundation Inspection
90.1-2016 Section # | Description | Design Value | Field Verified Value | Complies? (Yes/No) | Comments
5.5.3.3 | Below-grade wall insulation R-value.
5.8.1.2 | Below-grade wall insulation installed per manufacturer's instructions. | NA | NA
5.5.3.5 | Slab edge insulation R-value.
5.8.1.2 | Slab edge insulation installed per manufacturer's instructions and design. | NA | NA
5.8.1.7 | Exterior insulation protected against damage, sunlight, moisture, wind, landscaping and equipment maintenance activities. | NA | NA
5.8.1.7.3 | Insulation in contact with the ground has <=0.3% water absorption rate per ASTM C272. | NA | NA
6.3.2, 6.4.4.1, 6.4.4.2 | Piping, ducts and plenum are insulated and sealed when installed in or under a slab.
6.4.3.8 | Freeze protection and snow/ice melting system sensors installed for connection to controls. | NA | NA
6.4.4.1.5 | Bottom surface of floor structures incorporating radiant heating insulated to >=R-3.5. | NA | NA
end worksheet

## Framing Inspection
90.1-2016 Section # | Description | Design Value | Field Verified Value | Complies? (Yes/No) | Comments
5.4.3.1.2 | Continuous air barrier is wrapped, sealed, caulked, gasketed, and/or taped in an approved manner. | NA | NA
5.4.3.2 | Factory-built fenestration and doors are labeled as meeting air leakage requirements. | NA | NA
5.4.3.4 | Vestibules are installed where building entrances separate conditioned space from the exterior, and meet exterior envelope requirements. Doors have self-closing devices, and are >=7 ft apart. | NA | NA
5.5.4.3 | Fenestration U-Factor.
5.5.4.4.1 | Vertical fenestration SHGC value.
5.5.4.4.2 | Skylight SHGC value.
5.8.2 5.5.3.6 | U-factor of opaque doors associated with the building thermal envelope meets requirements. | NA | NA
end worksheet

## Insulation Inspection
90.1-2016 Section # | Description | Design Value | Field Verified Value | Complies? (Yes/No) | Comments
5.4.3.1.2 | All sources of air leakage in the building thermal envelope are sealed, caulked, gasketed or weather stripped to minimize air leakage. | NA | NA
5.5.3.1 | Roof R-value. For some roof systems, verification may need to occur during Framing Inspection.
5.8.1.2, 5.8.1.3 | Roof insulation installed per manufacturer's instructions. Blown or poured loose-fill insulation is installed only where the roof slope is <=3 in 12. | NA | NA
5.5.3.1 | Skylight curbs insulated to the level of roofs with insulation above deck or R-5. | NA | NA
5.5.3.2 | Above-grade wall insulation R-value.
5.8.1.2 | Above-grade wall insulation installed per manufacturer's instructions. | NA | NA
5.5.3.4 | Floor insulation R-value.
5.8.1.2 | Floor insulation installed per manufacturer's instructions. | NA | NA
5.8.1.4 | Eaves are baffled to deflect air above the insulation. | NA | NA
5.8.1.5 | Insulation is installed in substantial contact with the inside surface separating conditioned space from unconditioned space. | NA | NA
5.8.1.6 | Recessed equipment installed in building envelope assemblies does not compress the adjacent insulation. | NA | NA
5.8.1.7 | Exterior insulation is protected from damage with a protective material. | NA | NA
5.8.1.7.1 | Attics and mechanical rooms have insulation protected where adjacent to attic or equipment access. | NA | NA
5.8.1.7.2 | Foundation vents do not interfere with insulation. | NA | NA
5.8.1.8 | Insulation intended to meet the roof insulation requirements cannot be installed on top of a suspended ceiling. Mark this requirement compliant if insulation is installed accordingly. | NA | NA
end worksheet

## Plumbing Inspection
90.1-2016 Section # | Description | Complies? (Yes/No) | Comments
7.4.3 | Service hot-water piping systems insulated. Where piping is installed in or under a slab, verification may need to occur during Foundation Inspection.
7.4.4.1 | Temperature controls installed on service water heating systems (<=120 ºF to maximum temperature for intended use).
7.4.4.2 | Automatic time switches installed to automatically switch off the recirculating hot-water system or heat trace.
7.4.6 | Heat traps installed on non-circulating storage water tanks.
end worksheet

## Mechanical Inspection
90.1-2016 Section # | Description | Complies? (Yes/No) | Comments
6.4.1.4, 6.4.1.5 | HVAC equipment efficiency verified. Non-NAECA HVAC equipment labeled as meeting 90.1.
6.4.3.4.1 | Stair and elevator shaft vents have motorized dampers that automatically close.
6.4.3.4.2, 6.4.3.4.3 | Outdoor air and exhaust systems have motorized dampers that automatically shut when not in use and meet maximum leakage rates. Check gravity dampers where allowed.
6.4.3.4.4 | Ventilation fans >0.75 hp have automatic controls to shut off fan when not required.
6.4.3.9 | Demand control ventilation provided for spaces >500 ft2 and >25 people/1000 ft2 occupant density and served by systems with air side economizer, auto modulating outside air damper control or design airflow >3,000 cfm.
6.4.4.1.1 | Insulation exposed to weather protected from damage. Insulation outside of the conditioned space and associated with cooling systems is vapor retardant.
6.4.4.1.2 | HVAC ducts and plenums insulated (R-Value).
6.4.4.1.3 | HVAC piping insulation thickness.
6.4.4.1.4 | Thermally ineffective panel surfaces of sensible heating panels have insulation >= R-3.5.
6.4.4.2.1 | Ducts and plenums sealed based on static pressure and location.
6.4.4.2.2 | Ductwork operating >3 in. water column requires air leakage testing.
6.5.1.1.4 | Return air and outdoor air dampers meet minimum air leakage requirements.
6.5.1.1.5 | Means provided to relieve excess outside air during economizer operation.
6.5.1.4 | Economizer operation will not increase heating energy use during normal operation.
6.5.2.1 | Zone controls can limit simultaneous heating and cooling and sequence heating and cooling to each zone.
6.5.2.2.3 | Hydronic heat pump systems connected to a common water loop meet heat rejection and heat addition requirements.
6.5.2.3 | Dehumidification controls provided to prevent reheating, recooling, mixing of hot and cold airstreams or concurrent heating and cooling of the same airstream.
6.5.3.1.2 | HVAC fan motors not larger than the first available motor size greater than the bhp.
6.5.3.2.2 | VAV fans have static pressure sensors positioned so setpoint is no greater than 1.2 inches of water.
6.5.3.2.3 | Reset static pressure setpoint for DDC controlled VAV boxes reporting to central controller based on the zones requiring the most pressure.
6.5.3.3 | Multiple zone VAV systems with DDC of individual zone boxes shall include means to automatically reduce outdoor air.
6.5.3.5 | Multiple zone HVAC systems have supply air temperature reset controls.
6.5.4.3 | Reduce flow in pumping systems >10 hp to multiple chillers or boilers when others are shut down.
6.5.4.4 | Temperature reset by representative building loads in pumping systems for chiller and boiler systems >300,000 Btu/h.
6.5.4.5 | Two-position automatic valve interlocked to shut off water flow when hydronic heat pump with pumping system >10 hp is off.
6.5.4.4.2 | Hydronic heat pumps and water-cooled unitary air conditioners with pump systems >5 hp have controls or devices to reduce pump motor demand.
6.5.6.1 | Exhaust air energy recovery on systems required by Table 6.5.6.1.-1 or 2
6.5.7.2.1 | Replacement air introduced directly into the hood cavity of kitchen exhaust hoods shall not exceed 10% of the hood exhaust airflow rate.
6.5.7.2.2 | Kitchen hoods with a total exhaust airflow rate >5,000 cfm meet exhaust rate requirements.
6.5.7.1.4 | Kitchen hoods with a total exhaust airflow rate >5,000 cfm meet replacement air, ventilation system, or energy recovery requirements.
6.5.7.2.4 | Approved field test used to evaluate design air flow rates and demonstrate proper capture and containment of kitchen exhaust systems.
6.5.7.3 | Fume hoods exhaust systems >=15,000 cfm have VAV hood exhaust and supply systems, direct makeup air or heat recovery.
6.5.8.1 | Unenclosed spaces that are heated use only radiant heat.
7.4.2 | Service water heating equipment meets efficiency requirements.
7.5.1 | Combined space and water heating system not allowed unless standby loss less than calculated maximum. AHJ has approved or combined connected load <150 KBtu/h.
7.5.2 | Service water heating equipment used for space heating complies with the service water heating equipment requirements.
end worksheet

## Electrical Inspection
90.1-2016 Section # | Description | Complies? (Yes/No) | Comments
8.4.2 | At least 50% of all 125 volt 15- and 20-Amp receptacles, as required by 8.4.2, and 25% of the circuits for modular furniture are controlled by an automatic control device. And tested.
8.4.3.1 8.4.3.2 | Energy monitoring is installed and being recorded in buildings 25,000 sq ft or larger
9.4.1.1 | Automatic lighting controls installed per plans.
9.4.1.4 | Automatic lighting controls for exterior lighting installed.
9.6.2 | Additional interior lighting power allowed for special functions per the approved lighting plans and is automatically controlled and separated from general lighting.
8.4.1.1 8.4.1.2 | Does installation path follow design? If not, contractor to perform voltage drop calculations.

## Final Inspection
90.1-2016 Section # | Description | Complies? (Yes/No) | Comments
5.4.3.3 | Weatherseals installed on all loading dock cargo doors.
5.4.3.1.3 | Building pressure testing has been performed and documented. The use of any exceptions shall be documented
6.4.3.1.1 | Heating and cooling to each zone is controlled by a thermostat control.
6.4.3.1.2 | Thermostatic controls have a 5 °F deadband.
6.4.3.3.1 | HVAC systems equipped with at least one automatic shutdown control.
6.4.3.3.2 | Setback controls allow automatic restart and temporary operation as required for maintenance.
6.4.3.3.3 | Systems with air capacity >10,000 cfm include optimum start controls.
6.4.3.5 | Heat pump controls prevent supplemental electric resistance heat from coming on when not needed.
6.7.2.1 | Furnished HVAC as-built drawings submitted within 90 days of system acceptance.
6.7.2.2 | Furnished O&M manuals for HVAC systems.
6.7.2.3 | An air and/or hydronic system balancing report is provided for HVAC systems serving zones >5,000 ft2 of conditioned area.
6.7.2.4 | HVAC control systems have been tested to ensure proper operation, calibration and adjustment of controls.
7.4.4.3 | Public lavatory faucet water temperature <=110 ºF.
7.4.4.4 | Controls are installed that limit the operation of a recirculation pump installed to maintain temperature of a storage tank.
8.7.1 | Furnished as-built drawings for electric power systems within 30 days of system acceptance.
8.7.2 | Furnished O&M manuals for electrical power systems and equipment.
9.2.2.3 | Installed lamps and fixtures are consistent with what is shown on the approved lighting plans, which demonstrate proposed watts are less than or equal to allowed watts.
9.4.3 | Exterior lighting power is consistent with what is shown on the approved lighting plans, which demonstrate proposed watts are less than or equal to allowed watts.
end worksheet